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Manufacturer: HVP Security Shutters Ltd, 4 Grace Road West, Marsh Barton, Exeter, EX2 8PU. Tel: 01392 270 218. Fax: 01392 278 548. Email: info@hvpshutters.co.uk This email address is being protected from spam bots, you need Javascript enabled to view it [image: image1.png]


Website: www.hvpshutters.co.uk. 

  
Product reference: Fireguard FS50 Fire Resisting Roller Shutter
Description: 

1, 2 or 4 Hour Fire Resistance. Electric operation. The roller shutter is un-insulated and is manufactured in strict accordance with BS EN 1634-1 and compliant with harmonised standard BS EN 16034:2014; also BS EN 13241-1:2003. Electric operation by 1ph internal tubular motor. Curtain constructed from either 50mm flat or 76mm concave profile galvanised mild steel interlocking laths (gauge of laths being dependent on door size and hour rating), pressure riveted at each end of each alternate lath with steel end-locks. Galvanised, rolled inverted “T” section bottom rail to close against floor/counter. Guides to be 50mm or 65mm x 32mm galvanised steel. The motor is designed to drive the shutter curtain down upon receipt of a signal from the customer’s fire alarm or smoke/heat detector. Activation can also be by a thermal fusible link. With the exception of the angles, which are primer painted, the finish of the curtain, bottom rail, guides and canopy are galvanised A Safety Brake is fitted when required to comply with BSEN13241-1:2003.

The Fireguard FS50 is supplied with a Battery Back Up and FCP – Lite (or similar) Audio Visual Fire Control Panel  as standard.
Options:

· Powder Coat paint finish to most RAL colours






